## Summary
MICROLINK MONITORING & CONTROL SYSTEM
Master Point List — v1.0 — February 2026
Per 1MW Liquid-Cooled Compute Block — Standard Deployment Configuration
System | AI | AO | DI | DO | Calc | Total
§1 DATA CENTER OPERATIONS
Electrical Power Management | 28 | 4 | 18 | 6 | 5 | 61
Physical Security | 2 | 0 | 16 | 4 | 2 | 24
Environmental Monitoring | 22 | 2 | 14 | 0 | 4 | 42
Network & Connectivity | 8 | 0 | 10 | 0 | 6 | 24
Compute & IT Infrastructure | 16 | 2 | 8 | 2 | 4 | 32
§1 SUBTOTAL | 76 | 8 | 66 | 12 | 21 | 183
§2 THERMAL & HEAT RECOVERY
Loop 1 — IT Secondary (Compute Module) | 14 | 4 | 6 | 2 | 4 | 30
Loop 2 — MicroLink Primary Warm-Water | 20 | 6 | 10 | 4 | 6 | 46
Heat Export — Plate HX Interface | 12 | 2 | 8 | 2 | 4 | 28
Loop 3 — Host Process / Hot-Water | 6 | 0 | 6 | 0 | 3 | 15
Heat Rejection System (Fallback) | 10 | 4 | 8 | 2 | 3 | 27
Thermal Safety & Leak Detection | 6 | 0 | 16 | 2 | 2 | 26
§2 SUBTOTAL | 68 | 16 | 54 | 12 | 22 | 172
GRAND TOTAL | 144 | 24 | 120 | 24 | 43 | 355
I/O TYPE LEGEND
AI | Analog Input — continuous sensor reading (temp, pressure, flow, voltage, current)
AO | Analog Output — continuous control signal (valve position, VFD speed, setpoint)
DI | Digital Input — binary status (on/off, open/closed, alarm/normal, run/stop)
DO | Digital Output — binary command (start/stop, open/close, enable/disable)
Calc | Calculated / Virtual — derived from other points (ΔT, kWt, efficiency, COP)
ALARM PRIORITY LEGEND
P0 | CRITICAL — Immediate automated response + all-hands page. Equipment damage or safety risk.
P1 | MAJOR — 15-min response. Service degradation or impending failure. On-call engineer paged.
P2 | MINOR — 4-hour response. Performance deviation. NOC ticket auto-created.
P3 | INFO — Next-business-day review. Trending data, maintenance reminders.

## §1 DC Operations
§1 — DATA CENTER OPERATIONS POINT LIST
Point ID | System | Subsystem | Point Name | Description | I/O Type | Signal / Protocol | Range | Units | Alarm | Priority | Poll Rate | Hardware Ref | Notes
1.1 ELECTRICAL POWER MANAGEMENT
1.1.1 Intake Monitoring (Main Switchboard Demarc)
DC-PWR-001 | Electrical | Intake | Intake Voltage L1-L2-L3 | Three-phase RMS voltage at MicroLink main switchboard intake demarc point | AI | Modbus TCP | 0–500 | V | Y | P1 | 1s | PM-5350 | Per-phase monitoring; alarm on ±10% nominal
DC-PWR-002 | Electrical | Intake | Intake Current L1-L2-L3 | Three-phase RMS current at intake breaker CTs | AI | Modbus TCP | 0–2000 | A | Y | P1 | 1s | PM-5350 | Per-phase; alarm at 80% breaker rating
DC-PWR-003 | Electrical | Intake | Intake Frequency | Mains frequency at intake point | AI | Modbus TCP | 45–65 | Hz | Y | P1 | 1s | PM-5350 | Alarm on ±2% of nominal (50/60Hz)
DC-PWR-004 | Electrical | Intake | Intake Power Factor | Displacement PF at intake | AI | Modbus TCP | 0–1.0 | PF | Y | P2 | 5s | PM-5350 | Alarm below 0.90 lagging
DC-PWR-005 | Electrical | Intake | Intake Active Power | Total 3-phase active power at intake | AI | Modbus TCP | 0–1500 | kW | Y | P1 | 1s | PM-5350 | Primary load tracking — billing verification
DC-PWR-006 | Electrical | Intake | Intake Apparent Power | Total 3-phase apparent power at intake | AI | Modbus TCP | 0–1500 | kVA | N | — | 5s | PM-5350 | Capacity planning metric
DC-PWR-007 | Electrical | Intake | Intake THD Voltage | Total harmonic distortion on voltage waveform | AI | Modbus TCP | 0–30 | % | Y | P2 | 30s | PM-5350 | Alarm above 8% THD-V per IEEE 519
DC-PWR-008 | Electrical | Intake | Intake Energy Cumulative | Accumulated energy from utility meter — billing grade | AI | Modbus TCP | 0–999999 | kWh | N | — | 60s | PM-5350 | Revenue-grade metering for cost allocation
DC-PWR-009 | Electrical | Intake | Main Breaker Status | Main intake breaker position feedback (open/closed) | DI | Modbus TCP | 0/1 | — | Y | P0 | 1s | PM-5350 | P0 alarm on unexpected open
DC-PWR-010 | Electrical | Intake | Intake Earth Leakage | Residual current monitoring on intake | AI | Modbus TCP | 0–1000 | mA | Y | P1 | 5s | RCD Monitor | Alarm above 300mA; pre-trip warning at 150mA
1.1.2 UPS & Ride-Through
DC-PWR-011 | Electrical | UPS | UPS Input Voltage | UPS input bus voltage (all phases) | AI | SNMP v3 | 0–500 | V | Y | P1 | 5s | UPS-01 | Alarm on ±10% nominal
DC-PWR-012 | Electrical | UPS | UPS Output Voltage | UPS output bus voltage (all phases) | AI | SNMP v3 | 0–500 | V | Y | P0 | 1s | UPS-01 | Output quality — P0 on deviation >5%
DC-PWR-013 | Electrical | UPS | UPS Load Percentage | UPS load as % of rated capacity | AI | SNMP v3 | 0–100 | % | Y | P1 | 5s | UPS-01 | Alarm at 80%; P0 at 95%
DC-PWR-014 | Electrical | UPS | UPS Battery SOC | Battery state of charge | AI | SNMP v3 | 0–100 | % | Y | P1 | 30s | UPS-01 | Alarm below 80%; P0 below 50%
DC-PWR-015 | Electrical | UPS | UPS Estimated Runtime | Estimated remaining battery runtime at current load | AI | SNMP v3 | 0–999 | min | Y | P0 | 30s | UPS-01 | P0 below 5 min; P1 below 15 min
DC-PWR-016 | Electrical | UPS | UPS Bypass Active | UPS operating on bypass (mains direct) | DI | SNMP v3 | 0/1 | — | Y | P1 | 1s | UPS-01 | P1 alarm — reduced protection
DC-PWR-017 | Electrical | UPS | UPS On Battery | UPS discharging batteries — mains lost | DI | SNMP v3 | 0/1 | — | Y | P0 | 1s | UPS-01 | P0 — initiate generator start (Class B/C)
DC-PWR-018 | Electrical | UPS | UPS Battery Temperature | Internal battery compartment temperature | AI | SNMP v3 | 0–60 | °C | Y | P1 | 30s | UPS-01 | Alarm above 35°C; P0 above 45°C
DC-PWR-019 | Electrical | UPS | UPS Fault/Alarm | General UPS fault or alarm condition | DI | SNMP v3 | 0/1 | — | Y | P0 | 1s | UPS-01 | Any UPS fault = P0
1.1.3 Distribution Chain (PDU / Busway / Branches)
DC-PWR-020 | Electrical | Distribution | PDU-A Total Load | Total kW on PDU-A (primary feed to IT racks) | AI | Modbus TCP | 0–600 | kW | Y | P1 | 5s | PDU-A | Alarm at 80% rated capacity
DC-PWR-021 | Electrical | Distribution | PDU-B Total Load | Total kW on PDU-B (redundant feed to IT racks) | AI | Modbus TCP | 0–600 | kW | Y | P1 | 5s | PDU-B | Alarm at 80% rated capacity
DC-PWR-022 | Electrical | Distribution | Branch Circuit Load (×24) | Individual branch breaker current — per circuit | AI | Modbus TCP | 0–100 | A | Y | P2 | 10s | PDU-A/B | Per branch; 24 instances; alarm at 80%
DC-PWR-023 | Electrical | Distribution | Branch Breaker Trip (×24) | Branch breaker tripped status — per circuit | DI | Modbus TCP | 0/1 | — | Y | P1 | 1s | PDU-A/B | 24 instances; any trip = P1
DC-PWR-024 | Electrical | Distribution | PDU Input Breaker Status (×2) | Main input breaker status per PDU (A+B) | DI | Modbus TCP | 0/1 | — | Y | P0 | 1s | PDU-A/B | 2 instances; unexpected open = P0
DC-PWR-025 | Electrical | Distribution | TPM Power Feed Load | Power consumption of Thermal Plant Module equipment | AI | Modbus TCP | 0–150 | kW | Y | P2 | 10s | PM-TPM | Separate metering from IT load
DC-PWR-026 | Electrical | Distribution | Aux/BOP Power Load | Balance of plant — lighting, security, controls, comms | AI | Modbus TCP | 0–30 | kW | N | — | 60s | PM-AUX | Overhead tracking for PUE calculation
1.1.4 Generator (Class B/C Deployments)
DC-PWR-027 | Electrical | Generator | Generator Run Status | Engine running / stopped | DI | Modbus TCP | 0/1 | — | Y | P1 | 1s | GENSET-01 | Class B/C only
DC-PWR-028 | Electrical | Generator | Generator Output Power | Generator active power output | AI | Modbus TCP | 0–1500 | kW | Y | P1 | 5s | GENSET-01 | Load acceptance verification
DC-PWR-029 | Electrical | Generator | Generator Fuel Level | Fuel tank level — percentage | AI | 4-20mA | 0–100 | % | Y | P2 | 60s | FUEL-LEVEL | P2 below 50%; P1 below 25%
DC-PWR-030 | Electrical | Generator | ATS Position | Auto Transfer Switch position (Utility/Generator/Open) | DI | Modbus TCP | 0/1/2 | — | Y | P0 | 1s | ATS-01 | P0 on open transition >10s
DC-PWR-031 | Electrical | Generator | Generator Coolant Temp | Engine coolant temperature | AI | Modbus TCP | 0–120 | °C | Y | P1 | 10s | GENSET-01 | Alarm above 95°C
DC-PWR-032 | Electrical | Generator | Generator Oil Pressure | Engine oil pressure | AI | Modbus TCP | 0–800 | kPa | Y | P0 | 10s | GENSET-01 | P0 on low pressure — engine protect
DC-PWR-033 | Electrical | Generator | Generator Fault | General engine fault/alarm from controller | DI | Modbus TCP | 0/1 | — | Y | P0 | 1s | GENSET-01 | Any gen fault = P0
1.1.5 Calculated / Virtual — Electrical
DC-PWR-C01 | Electrical | Calculated | IT Load (Total) | Sum of PDU-A + PDU-B loads (net IT power) | Calc | Derived | 0–1200 | kW | Y | P1 | 5s | — | → dc-pwr-20 + dc-pwr-21
DC-PWR-C02 | Electrical | Calculated | Total Facility Load | IT + TPM + Aux/BOP power | Calc | Derived | 0–1500 | kW | N | — | 5s | — | → C1 + dc-pwr-25 + dc-pwr-26
DC-PWR-C03 | Electrical | Calculated | PUE (Power Usage Effectiveness) | Total facility power / IT load | Calc | Derived | 1.0–3.0 | ratio | Y | P2 | 60s | — | → C2 / C1; alarm above 1.25
DC-PWR-C04 | Electrical | Calculated | PDU Redundancy Balance | Load imbalance between PDU-A and PDU-B (% difference) | Calc | Derived | 0–100 | % | Y | P2 | 30s | — | Alarm if >20% imbalance
DC-PWR-C05 | Electrical | Calculated | Remaining kW Headroom | Contracted capacity minus current IT load | Calc | Derived | 0–1000 | kW | Y | P2 | 60s | — | Capacity sell-through tracking
1.2 PHYSICAL SECURITY
1.2.1 Access Control
DC-SEC-001 | Security | Access | Main Entry Door Status | Compute Module main entry door — open/closed reed switch | DI | Dry Contact | 0/1 | — | Y | P1 | 1s | DOOR-01 | P1 if open >60s without badge event
DC-SEC-002 | Security | Access | Main Entry Badge Reader | Badge-in event with credential ID and timestamp | DI | OSDP | Event | — | N | — | Event | READER-01 | Logged to access audit trail
DC-SEC-003 | Security | Access | Main Entry REX (Request to Exit) | PIR sensor for egress without badge | DI | Dry Contact | 0/1 | — | N | — | Event | REX-01 | Logged for occupancy tracking
DC-SEC-004 | Security | Access | TPM Entry Door Status | Thermal Plant Module entry door — open/closed | DI | Dry Contact | 0/1 | — | Y | P1 | 1s | DOOR-02 | Separate access zone from IT
DC-SEC-005 | Security | Access | TPM Badge Reader | Badge-in event for TPM zone | DI | OSDP | Event | — | N | — | Event | READER-02 | Different access permissions than IT zone
DC-SEC-006 | Security | Access | Emergency Exit Door Status | Emergency/fire exit door — open/closed + tamper | DI | Dry Contact | 0/1 | — | Y | P0 | 1s | DOOR-03 | P0 on unauthorized open outside fire alarm
DC-SEC-007 | Security | Access | Cabinet/Rack Lock Status (×n) | Individual rack cabinet lock — locked/unlocked | DI | OSDP | 0/1 | — | Y | P2 | 5s | LOCK-Rnn | Per colo rack; n = deployed rack count
DC-SEC-008 | Security | Access | Door Lock Command — Main | Electric strike/maglock release command | DO | Dry Contact | 0/1 | — | N | — | Event | STRIKE-01 | Command from access controller or MCS
DC-SEC-009 | Security | Access | Door Lock Command — TPM | TPM door lock release command | DO | Dry Contact | 0/1 | — | N | — | Event | STRIKE-02 | Independent from IT zone control
1.2.2 Video Surveillance
DC-SEC-010 | Security | CCTV | Camera Status — Main Entry (×1) | IP camera health status — online/offline | DI | ONVIF | 0/1 | — | Y | P2 | 30s | CAM-01 | P2 on camera offline >5 min
DC-SEC-011 | Security | CCTV | Camera Status — IT Room (×2) | IP camera health for IT rack area coverage | DI | ONVIF | 0/1 | — | Y | P2 | 30s | CAM-02/03 | 2 cameras for aisle coverage
DC-SEC-012 | Security | CCTV | Camera Status — TPM (×1) | IP camera health for Thermal Plant Module area | DI | ONVIF | 0/1 | — | Y | P2 | 30s | CAM-04 | Covers pumps, HX, valves
DC-SEC-013 | Security | CCTV | Camera Status — Exterior (×1) | IP camera for external approach and signage | DI | ONVIF | 0/1 | — | Y | P3 | 60s | CAM-05 | Perimeter awareness
DC-SEC-014 | Security | CCTV | NVR Storage Health | NVR disk health, remaining capacity, recording status | AI | SNMP | 0–100 | % | Y | P2 | 300s | NVR-01 | Alarm below 20% remaining capacity
DC-SEC-015 | Security | CCTV | Motion Detection Alert | Any camera motion event outside scheduled access | DI | ONVIF | Event | — | Y | P2 | Event | CAM-All | After-hours motion = auto P2
1.2.3 Intrusion Detection
DC-SEC-016 | Security | Intrusion | PIR Sensor — IT Room | Passive infrared occupancy/intrusion sensor | DI | Dry Contact | 0/1 | — | Y | P1 | 1s | PIR-01 | After-hours trigger = P1 + CCTV capture
DC-SEC-017 | Security | Intrusion | PIR Sensor — TPM | Passive infrared occupancy/intrusion — TPM zone | DI | Dry Contact | 0/1 | — | Y | P1 | 1s | PIR-02 | Independent zone
DC-SEC-018 | Security | Intrusion | Duress Alarm Button | Manual panic/duress button at entry | DI | Dry Contact | 0/1 | — | Y | P0 | 1s | PANIC-01 | P0 — silent alarm to NOC + local security
DC-SEC-019 | Security | Intrusion | Security Panel Fault | General fault from security panel (comms/power/tamper) | DI | Dry Contact | 0/1 | — | Y | P1 | 5s | SEC-PANEL | Security system self-monitoring
DC-SEC-020 | Security | Intrusion | Arm/Disarm Status | Security system arm/disarm state | DI | REST API | 0/1 | — | N | — | 5s | SEC-PANEL | Correlate with access events
DC-SEC-C01 | Security | Calculated | Occupancy Count (IT Zone) | Estimated occupancy from badge-in minus badge-out/REX events | Calc | Derived | 0–20 | ppl | Y | P3 | Event | — | Anomaly detection on unusual counts
DC-SEC-C02 | Security | Calculated | Occupancy Count (TPM Zone) | Estimated TPM zone occupancy | Calc | Derived | 0–10 | ppl | Y | P3 | Event | — | Lone worker awareness
1.3 ENVIRONMENTAL MONITORING
1.3.1 Temperature & Humidity — IT Zone
DC-ENV-001 | Environment | Temp/RH | Rack Inlet Temp — Cold Aisle (×n) | Per-rack cold aisle inlet temperature sensor | AI | Modbus/SNMP | 10–50 | °C | Y | P1 | 10s | TEMP-Rnn-I | n per rack; ASHRAE A1: 18–27°C; alarm ±3°C
DC-ENV-002 | Environment | Temp/RH | Rack Exhaust Temp — Hot Aisle (×n) | Per-rack hot aisle exhaust temperature | AI | Modbus/SNMP | 15–65 | °C | Y | P2 | 10s | TEMP-Rnn-E | Trending for cooling capacity verification
DC-ENV-003 | Environment | Temp/RH | Room Ambient Temp — IT | General IT room ambient temperature (overhead) | AI | BACnet/IP | 10–50 | °C | Y | P1 | 30s | TEMP-RM-01 | Backup reference; alarm at 30°C
DC-ENV-004 | Environment | Temp/RH | Room Humidity — IT | IT room relative humidity | AI | BACnet/IP | 0–100 | %RH | Y | P2 | 60s | RH-RM-01 | ASHRAE A1: 8–80% RH; alarm outside range
DC-ENV-005 | Environment | Temp/RH | Dew Point — IT Room | Calculated or sensed dew point | AI | BACnet/IP | -10–30 | °C | Y | P1 | 60s | RH-RM-01 | Condensation risk; alarm above 15°C DP
1.3.2 Temperature & Humidity — TPM Zone
DC-ENV-006 | Environment | Temp/RH | TPM Room Ambient Temp | Thermal Plant Module room ambient temperature | AI | BACnet/IP | 5–50 | °C | Y | P2 | 30s | TEMP-TPM-01 | Wider range than IT zone acceptable
DC-ENV-007 | Environment | Temp/RH | TPM Room Humidity | TPM room relative humidity | AI | BACnet/IP | 0–100 | %RH | Y | P3 | 120s | RH-TPM-01 | Less critical than IT zone
1.3.3 Water & Leak Detection
DC-ENV-008 | Environment | Leak | Leak Sensor — Under Rack Row A | Rope/spot leak sensor under rack row A | DI | Dry Contact | 0/1 | — | Y | P0 | 1s | LEAK-RA | P0 — immediate investigation
DC-ENV-009 | Environment | Leak | Leak Sensor — Under Rack Row B | Rope/spot leak sensor under rack row B | DI | Dry Contact | 0/1 | — | Y | P0 | 1s | LEAK-RB | P0 — liquid in IT zone
DC-ENV-010 | Environment | Leak | Leak Sensor — CDU Zone | Leak detection around CDU manifolds | DI | Dry Contact | 0/1 | — | Y | P0 | 1s | LEAK-CDU | P0 — trigger CDU isolation sequence
DC-ENV-011 | Environment | Leak | Leak Sensor — TPM Floor | TPM zone general floor leak detection | DI | Dry Contact | 0/1 | — | Y | P1 | 1s | LEAK-TPM | Expected environment — P1 not P0
DC-ENV-012 | Environment | Leak | Leak Sensor — Pipe Route | Pipe penetration / route between CM and TPM | DI | Dry Contact | 0/1 | — | Y | P0 | 1s | LEAK-PIPE | Critical isolation zone
1.3.4 Fire & Smoke Detection
DC-ENV-013 | Environment | Fire | Smoke Detector — IT Room (×n) | Addressable smoke detectors in IT zone | DI | Fire Panel | 0/1 | — | Y | P0 | 1s | SMOKE-IT-nn | Fire panel integration via relay or Modbus
DC-ENV-014 | Environment | Fire | Smoke Detector — TPM (×n) | Addressable smoke detectors in TPM zone | DI | Fire Panel | 0/1 | — | Y | P0 | 1s | SMOKE-TPM-nn | Separate zone from IT
DC-ENV-015 | Environment | Fire | VESDA Alert Level | Very Early Smoke Detection — alert/action/fire levels | AI | Modbus TCP | 0–3 | Level | Y | P0 | 1s | VESDA-01 | 0=Normal, 1=Alert, 2=Action, 3=Fire
DC-ENV-016 | Environment | Fire | Fire Panel General Alarm | Fire alarm panel in alarm state | DI | Dry Contact | 0/1 | — | Y | P0 | 1s | FIRE-PANEL | P0 — immediate action; coordinate with host
DC-ENV-017 | Environment | Fire | Fire Panel Fault | Fire system fault (wiring, detector, battery) | DI | Dry Contact | 0/1 | — | Y | P1 | 5s | FIRE-PANEL | Regulatory compliance monitoring
DC-ENV-018 | Environment | Fire | Suppression System Armed | Gas/clean agent suppression system arm status | DI | Dry Contact | 0/1 | — | Y | P1 | 30s | SUPP-01 | Alert if disarmed outside maintenance
DC-ENV-019 | Environment | Fire | Suppression Discharged | Suppression agent has been released | DI | Dry Contact | 0/1 | — | Y | P0 | 1s | SUPP-01 | P0 — room entry restriction
1.3.5 Air Quality
DC-ENV-020 | Environment | Air Quality | Particulate PM2.5 — IT | Fine particulate matter in IT zone | AI | Modbus | 0–500 | µg/m³ | Y | P2 | 120s | AQ-IT-01 | ISO 14644; alarm above 100 µg/m³
DC-ENV-021 | Environment | Air Quality | CO Level — Generator Area | Carbon monoxide near generator exhaust | AI | 4-20mA | 0–500 | ppm | Y | P0 | 10s | CO-GEN-01 | P0 above 50 ppm; Class B/C only
DC-ENV-022 | Environment | Air Quality | Glycol Vapour — TPM | VOC/glycol vapor detection in TPM zone | AI | 4-20mA | 0–100 | ppm | Y | P1 | 30s | VOC-TPM-01 | Glycol leak indicator in thermal zone
1.3.6 Ventilation & HVAC
DC-ENV-023 | Environment | HVAC | HVAC Supply Air Temp — IT | Supply air temperature (if supplementary AC present) | AI | BACnet/IP | 10–30 | °C | Y | P2 | 30s | AHU-IT-01 | For non-liquid-cooled components
DC-ENV-024 | Environment | HVAC | HVAC Fan Status — IT | Fan run/stop status | DI | BACnet/IP | 0/1 | — | Y | P2 | 10s | AHU-IT-01 | Alarm on unexpected stop
DC-ENV-025 | Environment | HVAC | TPM Exhaust Fan Status | TPM zone ventilation fan — run/stop | DI | Dry Contact | 0/1 | — | Y | P2 | 10s | FAN-TPM-01 | Ventilation for glycol vapour management
DC-ENV-026 | Environment | HVAC | TPM Exhaust Fan Command | Start/stop command for TPM exhaust fan | DO | Dry Contact | 0/1 | — | N | — | Event | FAN-TPM-01 | Auto-start on VOC alarm
DC-ENV-C01 | Environment | Calculated | ΔT Rack Average (Hot-Cold) | Average temperature rise across IT racks | Calc | Derived | 0–30 | °C | Y | P2 | 30s | — | Cooling effectiveness indicator
DC-ENV-C02 | Environment | Calculated | Thermal Map Score | Composite score from all zone sensors — hotspot indicator | Calc | Derived | 0–100 | score | Y | P2 | 60s | — | ML anomaly detection candidate
DC-ENV-C03 | Environment | Calculated | Airside Cooling Fraction | % of total heat removed by air vs liquid | Calc | Derived | 0–100 | % | N | — | 300s | — | Design verification; should be <15%
DC-ENV-C04 | Environment | Calculated | EUE (Energy Usage Effectiveness) | Extended metric including external energy recovery | Calc | Derived | 0–2.0 | ratio | N | — | 300s | — | Accounts for thermal export credit
1.4 NETWORK & CONNECTIVITY
1.4.1 WAN / Route Diversity
DC-NET-001 | Network | WAN | Route A — Link State | Primary diverse fiber path — up/down | DI | SNMP v3 | 0/1 | — | Y | P0 | 5s | RTR-01 | P0 on down — single route exposure
DC-NET-002 | Network | WAN | Route B — Link State | Secondary diverse fiber path — up/down | DI | SNMP v3 | 0/1 | — | Y | P0 | 5s | RTR-01 | P0 if both routes down = isolated
DC-NET-003 | Network | WAN | Route A — Optical Power | SFP/QSFP receive optical power — Route A | AI | SNMP v3 | -40–0 | dBm | Y | P2 | 30s | RTR-01 | Alarm on degradation trend
DC-NET-004 | Network | WAN | Route B — Optical Power | SFP/QSFP receive optical power — Route B | AI | SNMP v3 | -40–0 | dBm | Y | P2 | 30s | RTR-01 | Pre-failure warning on optics
DC-NET-005 | Network | WAN | Route A — CRC/FCS Errors | Layer 2 error rate on Route A interface | AI | SNMP v3 | 0–999 | err/s | Y | P2 | 60s | RTR-01 | Alarm above baseline + 3 std dev
DC-NET-006 | Network | WAN | Route B — CRC/FCS Errors | Layer 2 error rate on Route B interface | AI | SNMP v3 | 0–999 | err/s | Y | P2 | 60s | RTR-01
1.4.2 Performance & Latency
DC-NET-007 | Network | Performance | Latency to MMR Handoff | Round-trip latency to colo MMR or IX point | AI | ICMP/gRPC | 0–100 | ms | Y | P2 | 30s | PROBE-01 | SLA baseline compliance
DC-NET-008 | Network | Performance | Jitter — Route A | Packet jitter on primary route | AI | gRPC | 0–50 | ms | Y | P2 | 30s | PROBE-01 | Quality-of-service indicator
DC-NET-009 | Network | Performance | Packet Loss % | Measured packet loss across both routes | AI | ICMP/gRPC | 0–100 | % | Y | P1 | 30s | PROBE-01 | P1 above 0.1% loss
1.4.3 OOB & Management Network
DC-NET-010 | Network | OOB | OOB Management Link | Out-of-band management network link state | DI | SNMP v3 | 0/1 | — | Y | P1 | 10s | OOB-SW-01 | Independent from customer data plane
DC-NET-011 | Network | OOB | Edge Gateway Heartbeat | MCS edge controller heartbeat to central NOC | DI | MQTT | 0/1 | — | Y | P0 | 10s | EDGE-GW | P0 — loss of remote monitoring
DC-NET-012 | Network | OOB | VPN Tunnel Status | Site-to-NOC VPN tunnel state | DI | SNMP v3 | 0/1 | — | Y | P1 | 30s | FW-01 | Backup via cellular if primary down
DC-NET-C01 | Network | Calculated | Route Diversity Score | Composite availability of dual diverse routes | Calc | Derived | 0–100 | % | Y | P1 | 60s | — | 100%=both up; 50%=one down; 0%=isolated
DC-NET-C02 | Network | Calculated | SLA Compliance — Latency | % of time latency within SLA threshold | Calc | Derived | 0–100 | % | Y | P2 | 300s | — | Rolling 30-day window
DC-NET-C03 | Network | Calculated | Network Availability — Monthly | Uptime percentage for network services | Calc | Derived | 0–100 | % | Y | P1 | 300s | — | SLA reporting; target 99.99%
DC-NET-C04 | Network | Calculated | MCS Connectivity Score | Composite of OOB + VPN + heartbeat for remote mgmt | Calc | Derived | 0–100 | % | Y | P0 | 30s | — | 0% = site dark to NOC
DC-NET-C05 | Network | Calculated | Bandwidth Utilization — Route A | Traffic utilization as % of port capacity | Calc | Derived | 0–100 | % | Y | P2 | 60s | — | Capacity planning; alarm at 80%
DC-NET-C06 | Network | Calculated | Bandwidth Utilization — Route B | Traffic utilization as % of port capacity | Calc | Derived | 0–100 | % | Y | P2 | 60s | —
1.5 COMPUTE & IT INFRASTRUCTURE
1.5.1 Rack-Level Telemetry
DC-IT-001 | Compute | Rack | Rack Power — Per Rack (×n) | Individual rack total power consumption via intelligent PDU | AI | SNMP/Modbus | 0–200 | kW | Y | P2 | 10s | iPDU-Rnn | n = deployed racks; alarm at rated capacity
DC-IT-002 | Compute | Rack | Rack Inlet Coolant Temp (×n) | Liquid coolant inlet temp at rack manifold | AI | Modbus TCP | 10–40 | °C | Y | P1 | 5s | TEMP-RCL-nn | Alarm if supply temp rises above setpoint +3°C
DC-IT-003 | Compute | Rack | Rack Outlet Coolant Temp (×n) | Liquid coolant outlet temp at rack manifold | AI | Modbus TCP | 20–70 | °C | Y | P2 | 5s | TEMP-RCL-nn | Used for ΔT and kWt calculation
DC-IT-004 | Compute | Rack | Rack Coolant Flow (×n) | Coolant volumetric flow rate per rack manifold | AI | Modbus TCP | 0–50 | L/min | Y | P1 | 10s | FLOW-RCL-nn | Low flow = P1; zero flow = P0
1.5.2 CDU Monitoring
DC-IT-005 | Compute | CDU | CDU Status (×n) | CDU operational status — run/stop/fault | DI | Modbus TCP | 0/1/2 | — | Y | P0 | 5s | CDU-nn | P0 on fault; n = CDU count
DC-IT-006 | Compute | CDU | CDU Primary Supply Temp | CDU primary-side coolant supply temperature | AI | Modbus TCP | 10–50 | °C | Y | P1 | 5s | CDU-nn | IT-side setpoint verification
DC-IT-007 | Compute | CDU | CDU Primary Return Temp | CDU primary-side coolant return temperature | AI | Modbus TCP | 20–70 | °C | Y | P2 | 5s | CDU-nn | Heat pickup verification
DC-IT-008 | Compute | CDU | CDU Secondary Supply Temp | CDU secondary-side (building loop) supply temperature | AI | Modbus TCP | 15–55 | °C | Y | P1 | 5s | CDU-nn | Cross-loop reference
DC-IT-009 | Compute | CDU | CDU Secondary Return Temp | CDU secondary-side return temperature | AI | Modbus TCP | 25–65 | °C | Y | P2 | 5s | CDU-nn
DC-IT-010 | Compute | CDU | CDU Flow Rate | CDU primary-side total flow rate | AI | Modbus TCP | 0–200 | L/min | Y | P1 | 10s | CDU-nn | Low flow alarm
DC-IT-011 | Compute | CDU | CDU Pump Speed/VFD | CDU pump speed or VFD frequency | AI | Modbus TCP | 0–60 | Hz | N | — | 30s | CDU-nn | Performance monitoring
DC-IT-012 | Compute | CDU | CDU Reservoir Level | Coolant reservoir level in CDU | AI | Modbus TCP | 0–100 | % | Y | P1 | 60s | CDU-nn | Low level = possible leak
DC-IT-013 | Compute | CDU | CDU Pump Command | CDU pump start/stop command | DO | Modbus TCP | 0/1 | — | N | — | Event | CDU-nn | Manual override capability
DC-IT-014 | Compute | CDU | CDU Speed Setpoint | CDU pump speed setpoint | AO | Modbus TCP | 0–60 | Hz | N | — | Event | CDU-nn | Control output for flow regulation
1.5.3 Capacity Management (Calculated)
DC-IT-C01 | Compute | Calculated | Total IT kW Utilized | Sum of all rack power readings | Calc | Derived | 0–1200 | kW | Y | P2 | 30s | — | Sell-through tracking
DC-IT-C02 | Compute | Calculated | IT kW Available / Headroom | Contracted capacity minus utilized | Calc | Derived | 0–1000 | kW | Y | P2 | 60s | — | Sales pipeline metric
DC-IT-C03 | Compute | Calculated | Cooling Capacity Utilized | Total thermal load vs cooling capacity (kWt) | Calc | Derived | 0–100 | % | Y | P1 | 60s | — | Alarm at 85% thermal capacity
DC-IT-C04 | Compute | Calculated | Rack Units Available | Total free RU across all racks | Calc | Derived | 0–999 | RU | N | — | 300s | — | Inventory for colo sales
DC-IT-C05 | Compute | Calculated | Per-Rack kWt Thermal Load (×n) | Calculated thermal load per rack from ΔT × flow | Calc | Derived | 0–200 | kWt | N | — | 10s | — | → δt × flow × Cp; per rack
DC-IT-C06 | Compute | Calculated | CDU COP / Effectiveness | CDU cooling effectiveness metric | Calc | Derived | 0–50 | ratio | N | — | 300s | — | Design verification

## §2 Thermal & Heat
§2 — THERMAL & HEAT RECOVERY POINT LIST
Point ID | System | Subsystem | Point Name | Description | I/O Type | Signal / Protocol | Range | Units | Alarm | Priority | Poll Rate | Hardware Ref | Notes
2.1 LOOP 1 — IT SECONDARY (COMPUTE MODULE)
2.1.1 Direct-to-Chip / Server-Side Cooling
TH-L1-001 | Thermal | Loop 1 | L1 Supply Temperature | IT secondary loop coolant supply temp (from CDU to servers) | AI | Modbus TCP | 15–40 | °C | Y | P1 | 5s | TEMP-L1S | Setpoint: ~25–35°C; alarm ±5°C of SP
TH-L1-002 | Thermal | Loop 1 | L1 Return Temperature | IT secondary loop coolant return temp (from servers to CDU) | AI | Modbus TCP | 25–70 | °C | Y | P1 | 5s | TEMP-L1R | Higher = more heat captured
TH-L1-003 | Thermal | Loop 1 | L1 Flow Rate | IT secondary loop total volumetric flow | AI | Modbus TCP | 0–300 | L/min | Y | P1 | 5s | FLOW-L1 | Low flow alarm; zero = P0
TH-L1-004 | Thermal | Loop 1 | L1 Differential Pressure | ΔP across IT secondary loop manifold | AI | 4-20mA | 0–200 | kPa | Y | P2 | 10s | DP-L1 | High ΔP = blockage / filter load
TH-L1-005 | Thermal | Loop 1 | L1 Pressure — Supply | Static pressure on supply side | AI | 4-20mA | 0–600 | kPa | Y | P2 | 10s | P-L1S | Leak detection; low pressure alarm
TH-L1-006 | Thermal | Loop 1 | L1 Pressure — Return | Static pressure on return side | AI | 4-20mA | 0–600 | kPa | Y | P2 | 10s | P-L1R
TH-L1-007 | Thermal | Loop 1 | L1 Coolant Conductivity | Electrical conductivity of IT-side coolant — purity check | AI | 4-20mA | 0–100 | µS/cm | Y | P2 | 300s | COND-L1 | Clean loop; alarm above 10 µS/cm
TH-L1-008 | Thermal | Loop 1 | L1 Reservoir Level | Expansion / makeup reservoir level for Loop 1 | AI | 4-20mA | 0–100 | % | Y | P1 | 60s | LEVEL-L1 | Low level = leak indication
2.1.2 Loop 1 Controls & Calculated
TH-L1-009 | Thermal | Loop 1 | L1 Pump Status (×n) | IT-side circulation pump run/stop/fault | DI | Modbus TCP | 0/1/2 | — | Y | P0 | 5s | PUMP-L1-nn | N+1 redundant; P0 on all-fault
TH-L1-010 | Thermal | Loop 1 | L1 Pump Speed Command | VFD speed setpoint for L1 pump | AO | Modbus TCP | 0–60 | Hz | N | — | Event | VFD-L1 | Flow regulation control output
TH-L1-011 | Thermal | Loop 1 | L1 Pump Speed Feedback | Actual VFD speed feedback | AI | Modbus TCP | 0–60 | Hz | N | — | 5s | VFD-L1 | Command vs feedback comparison
TH-L1-012 | Thermal | Loop 1 | L1 Pump Motor Current | Pump motor current draw — health indicator | AI | Modbus TCP | 0–100 | A | Y | P2 | 30s | VFD-L1 | Trending for bearing/impeller wear
TH-L1-013 | Thermal | Loop 1 | L1 Isolation Valve — Supply | Motorized isolation valve on L1 supply | DI | Dry Contact | 0/1 | — | Y | P0 | 1s | MOV-L1S | P0 if closed unexpectedly
TH-L1-014 | Thermal | Loop 1 | L1 Isolation Valve Cmd — Supply | Command to open/close L1 supply isolation valve | DO | Dry Contact | 0/1 | — | N | — | Event | MOV-L1S | Emergency isolation capability
TH-L1-C01 | Thermal | Loop 1 Calc | L1 ΔT (Return - Supply) | Temperature difference across Loop 1 | Calc | Derived | 0–40 | °C | Y | P2 | 5s | — | → th-L1-2 − TH-L1-001
TH-L1-C02 | Thermal | Loop 1 Calc | L1 Thermal Power (kWt) | Heat captured by Loop 1: ΔT × flow × Cp | Calc | Derived | 0–1200 | kWt | Y | P2 | 5s | — | Primary performance KPI
TH-L1-C03 | Thermal | Loop 1 Calc | L1 Heat Capture Ratio | L1 kWt / IT kW electrical — cooling effectiveness | Calc | Derived | 0–1.0 | ratio | Y | P2 | 60s | — | Should be 0.85–0.95 for liquid-cooled
TH-L1-C04 | Thermal | Loop 1 Calc | L1 Pump Power Consumption | Power drawn by L1 circulation pumps | Calc | Derived | 0–20 | kW | N | — | 60s | — | Parasitic load tracking
2.2 LOOP 2 — MICROLINK PRIMARY WARM-WATER LOOP
2.2.1 Primary Loop Temperatures & Flow
TH-L2-001 | Thermal | Loop 2 | L2 Supply Temperature | Primary warm-water loop supply temp (from CDU secondary to HX/reject) | AI | Modbus TCP | 25–65 | °C | Y | P1 | 5s | TEMP-L2S | Key operating parameter
TH-L2-002 | Thermal | Loop 2 | L2 Return Temperature | Primary loop return temp (from HX/reject back to CDU secondary) | AI | Modbus TCP | 15–50 | °C | Y | P1 | 5s | TEMP-L2R | Determines export ΔT available
TH-L2-003 | Thermal | Loop 2 | L2 Flow Rate | Primary loop volumetric flow — electromagnetic meter | AI | Modbus TCP | 0–500 | L/min | Y | P1 | 5s | FLOW-L2 | Billing-grade accuracy required
TH-L2-004 | Thermal | Loop 2 | L2 Differential Pressure | ΔP across primary loop circuit | AI | 4-20mA | 0–300 | kPa | Y | P2 | 10s | DP-L2 | Pump performance verification
TH-L2-005 | Thermal | Loop 2 | L2 Static Pressure — Supply | Static pressure on L2 supply header | AI | 4-20mA | 0–1000 | kPa | Y | P1 | 10s | P-L2S | Leak detection / integrity
TH-L2-006 | Thermal | Loop 2 | L2 Static Pressure — Return | Static pressure on L2 return header | AI | 4-20mA | 0–1000 | kPa | Y | P1 | 10s | P-L2R
2.2.2 Primary Pump Station
TH-L2-007 | Thermal | Loop 2 | L2 Pump-A Status | Primary pump A — run/stop/fault | DI | Modbus TCP | 0/1/2 | — | Y | P0 | 5s | PUMP-L2A | N+1 duty/standby arrangement
TH-L2-008 | Thermal | Loop 2 | L2 Pump-B Status | Primary pump B — run/stop/fault (standby) | DI | Modbus TCP | 0/1/2 | — | Y | P0 | 5s | PUMP-L2B | Auto-changeover on duty fault
TH-L2-009 | Thermal | Loop 2 | L2 Pump Speed Command | VFD speed setpoint for duty pump | AO | Modbus TCP | 0–60 | Hz | N | — | Event | VFD-L2 | ΔP or flow control
TH-L2-010 | Thermal | Loop 2 | L2 Pump Speed Feedback | VFD actual speed feedback | AI | Modbus TCP | 0–60 | Hz | N | — | 5s | VFD-L2
TH-L2-011 | Thermal | Loop 2 | L2 Pump Motor Current (×2) | Motor current for each pump — health trending | AI | Modbus TCP | 0–100 | A | Y | P2 | 30s | VFD-L2A/B | Bearing wear / impeller degradation
TH-L2-012 | Thermal | Loop 2 | L2 Pump Vibration (×2) | Vibration sensor on each pump — predictive maintenance | AI | 4-20mA | 0–50 | mm/s | Y | P2 | 60s | VIB-L2A/B | Alarm above ISO 10816 limits
TH-L2-013 | Thermal | Loop 2 | L2 Pump Runtime Hours (×2) | Cumulative runtime for maintenance scheduling | AI | Modbus TCP | 0–99999 | hrs | Y | P3 | 3600s | VFD-L2A/B | Alarm at service interval
TH-L2-014 | Thermal | Loop 2 | L2 Pump Start/Stop Cmd (×2) | Start/stop command per pump | DO | Modbus TCP | 0/1 | — | N | — | Event | VFD-L2A/B | Manual override / auto changeover
2.2.3 Water Chemistry & System Health
TH-L2-015 | Thermal | Loop 2 | L2 Glycol Concentration | Propylene glycol concentration in primary loop | AI | 4-20mA | 0–60 | % | Y | P2 | 3600s | GLYCOL-L2 | Design spec: 30–40%; alarm outside range
TH-L2-016 | Thermal | Loop 2 | L2 pH Level | Primary loop water pH | AI | 4-20mA | 0–14 | pH | Y | P2 | 3600s | PH-L2 | Target 7.5–9.0; alarm outside range
TH-L2-017 | Thermal | Loop 2 | L2 Conductivity | Primary loop water conductivity — contamination indicator | AI | 4-20mA | 0–5000 | µS/cm | Y | P2 | 3600s | COND-L2 | Different spec from clean L1 loop
TH-L2-018 | Thermal | Loop 2 | L2 Expansion Vessel Pressure | Pressurization system vessel air charge pressure | AI | 4-20mA | 0–600 | kPa | Y | P1 | 300s | EXP-L2 | System integrity indicator
TH-L2-019 | Thermal | Loop 2 | L2 Auto-Fill Valve Status | Make-up water auto-fill valve — open/closed | DI | Dry Contact | 0/1 | — | Y | P2 | 30s | FILL-L2 | Frequent fills = possible leak
TH-L2-020 | Thermal | Loop 2 | L2 Auto-Fill Accumulated | Cumulative make-up water added | AI | Modbus TCP | 0–9999 | L | Y | P2 | 300s | FLOW-FILL | Trending for slow leak detection
TH-L2-021 | Thermal | Loop 2 | L2 Air/Dirt Separator Status | Air separator operational status | DI | Dry Contact | 0/1 | — | Y | P3 | 300s | AIRDIRT-L2 | Maintenance indicator
2.2.4 Loop 2 Calculated Points
TH-L2-C01 | Thermal | Loop 2 Calc | L2 ΔT (Supply - Return) | Primary loop temperature difference | Calc | Derived | 0–30 | °C | Y | P2 | 5s | — | → th-L2-1 − TH-L2-002
TH-L2-C02 | Thermal | Loop 2 Calc | L2 Thermal Power (kWt) | Heat transported by primary loop | Calc | Derived | 0–1200 | kWt | Y | P1 | 5s | — | Primary performance metric
TH-L2-C03 | Thermal | Loop 2 Calc | L2 Pump Power (Total) | Total electrical power consumed by L2 pumps | Calc | Derived | 0–30 | kW | N | — | 60s | — | Parasitic load
TH-L2-C04 | Thermal | Loop 2 Calc | L2 Transport COP | kWt transported / kW pump power consumed | Calc | Derived | 0–100 | ratio | N | — | 300s | — | → C2/C3; efficiency of thermal transport
TH-L2-C05 | Thermal | Loop 2 Calc | L2 Leak Rate Estimate | Estimated leak rate from fill accumulation trend | Calc | Derived | 0–100 | L/day | Y | P1 | 3600s | — | Alarm above 5 L/day
TH-L2-C06 | Thermal | Loop 2 Calc | L2 System Pressure Trend | Pressure rate of change — integrity monitoring | Calc | Derived | -50–50 | kPa/h | Y | P1 | 300s | — | Rapid drop = breach
2.3 HEAT EXPORT — PLATE HEAT EXCHANGER INTERFACE
2.3.1 HX Performance Monitoring
TH-HX-001 | Thermal | Heat Export | HX Primary Inlet Temp | Hot side inlet temp — from L2 supply | AI | Modbus TCP | 30–65 | °C | Y | P2 | 5s | TEMP-HX-PI | MicroLink side — our fluid
TH-HX-002 | Thermal | Heat Export | HX Primary Outlet Temp | Hot side outlet temp — returned to L2 | AI | Modbus TCP | 15–50 | °C | Y | P2 | 5s | TEMP-HX-PO | Should approach host return temp
TH-HX-003 | Thermal | Heat Export | HX Secondary Inlet Temp | Cold side inlet temp — host return water | AI | Modbus TCP | 10–45 | °C | Y | P1 | 5s | TEMP-HX-SI | Host return conditions monitoring
TH-HX-004 | Thermal | Heat Export | HX Secondary Outlet Temp | Cold side outlet temp — heated host water | AI | Modbus TCP | 20–60 | °C | Y | P1 | 5s | TEMP-HX-SO | Host delivery temp verification
TH-HX-005 | Thermal | Heat Export | HX Primary Flow Rate | Flow through primary (MicroLink) side of HX | AI | Modbus TCP | 0–500 | L/min | Y | P1 | 5s | FLOW-HX-P | Billing-grade metering
TH-HX-006 | Thermal | Heat Export | HX Secondary Flow Rate | Flow through secondary (host) side of HX | AI | Modbus TCP | 0–500 | L/min | Y | P2 | 5s | FLOW-HX-S | Host-side reference
TH-HX-007 | Thermal | Heat Export | HX Primary ΔP | Pressure drop across HX primary side | AI | 4-20mA | 0–200 | kPa | Y | P2 | 60s | DP-HX-P | Fouling indicator — trend over time
TH-HX-008 | Thermal | Heat Export | HX Secondary ΔP | Pressure drop across HX secondary side | AI | 4-20mA | 0–200 | kPa | Y | P2 | 60s | DP-HX-S | Host-side fouling indicator
2.3.2 Isolation & Protection Valves
TH-HX-009 | Thermal | Heat Export | HX ML-Side Isolation Valve | MicroLink isolation valve — position feedback | DI | Dry Contact | 0/1 | — | Y | P0 | 1s | MOV-HX-ML | Hydraulic isolation of ML loop from HX
TH-HX-010 | Thermal | Heat Export | HX ML-Side Valve Command | Command to open/close ML isolation valve | DO | Dry Contact | 0/1 | — | N | — | Event | MOV-HX-ML | Mode transition actuator
TH-HX-011 | Thermal | Heat Export | HX Host-Side Isolation Valve | Host-side isolation valve — position feedback | DI | Dry Contact | 0/1 | — | Y | P1 | 1s | MOV-HX-HOST | Host boundary control
TH-HX-012 | Thermal | Heat Export | HX Host-Side Valve Command | Command to open/close host isolation valve | DO | Dry Contact | 0/1 | — | N | — | Event | MOV-HX-HOST | Coordinated with host demand signal
TH-HX-013 | Thermal | Heat Export | HX Bypass 3-Way Valve Position | 3-way diverting valve position — export vs reject path | AI | 4-20mA | 0–100 | % | Y | P1 | 5s | MOV-HX-3W | 0%=full reject; 100%=full export
TH-HX-014 | Thermal | Heat Export | HX Bypass Valve Command | 3-way valve position setpoint | AO | 4-20mA | 0–100 | % | N | — | Event | MOV-HX-3W | Mode state engine control output
TH-HX-015 | Thermal | Heat Export | Backflow Prevention Status | Check valve / backflow preventer health | DI | Dry Contact | 0/1 | — | Y | P1 | 300s | BFP-HX | Cross-contamination protection
2.3.3 Heat Export Calculated / Billing
TH-HX-C01 | Thermal | HX Calc | Exported Thermal Power (kWt) | Real-time heat export rate to host | Calc | Derived | 0–1200 | kWt | Y | P1 | 5s | — | → δt × flow × Cp (primary side)
TH-HX-C02 | Thermal | HX Calc | Cumulative Exported Energy (MWht) | Total thermal energy exported — billing accumulator | Calc | Derived | 0–999999 | MWht | N | — | 5s | — | Revenue metering — latch on rollover
TH-HX-C03 | Thermal | HX Calc | HX Approach Temperature | Minimum ΔT approach in HX — fouling indicator | Calc | Derived | 0–15 | °C | Y | P2 | 60s | — | → hx-2 − HX-003; alarm if increasing
TH-HX-C04 | Thermal | HX Calc | HX Fouling Factor Estimate | Estimated fouling factor from UA degradation | Calc | Derived | 0–1.0 | — | Y | P2 | 3600s | — | CIP/maintenance trigger
TH-HX-C05 | Thermal | HX Calc | Export Revenue (Estimated) | Estimated revenue from thermal export at contracted $/MWht | Calc | Derived | 0–9999 | $/day | N | — | 3600s | — | Dashboard metric; not billing-grade
TH-HX-C06 | Thermal | HX Calc | Host Delivery Compliance % | % of time host receives heat within contracted temp range | Calc | Derived | 0–100 | % | Y | P2 | 300s | — | SLA compliance metric
2.4 LOOP 3 — HOST PROCESS / HOT-WATER (READ-ONLY INTERFACE)
TH-L3-001 | Thermal | Loop 3 | Host Demand Signal | Host heat demand — active/inactive (binary) | DI | BACnet/IP | 0/1 | — | Y | P2 | 10s | HOST-BMS | Primary mode trigger input
TH-L3-002 | Thermal | Loop 3 | Host Temperature Setpoint Request | Host requested supply temperature setpoint | AI | BACnet/IP | 30–70 | °C | Y | P2 | 30s | HOST-BMS | Guidance only — ML controls HX independently
TH-L3-003 | Thermal | Loop 3 | Host Flow Status | Host-side circulation active/inactive | DI | BACnet/IP | 0/1 | — | Y | P2 | 10s | HOST-BMS | No host flow = cannot export
TH-L3-004 | Thermal | Loop 3 | Host Return Temp (at boundary) | Host return water temperature measured at ML boundary | AI | Modbus TCP | 5–50 | °C | Y | P1 | 5s | TEMP-L3R | ML-owned sensor at interface point
TH-L3-005 | Thermal | Loop 3 | Host Return Pressure | Host return water pressure at boundary | AI | 4-20mA | 0–1000 | kPa | Y | P1 | 10s | P-L3R | Overpressure / underpressure protection
TH-L3-006 | Thermal | Loop 3 | Host Contamination Conductivity | Conductivity sensor at boundary — cross-contamination check | AI | 4-20mA | 0–5000 | µS/cm | Y | P0 | 60s | COND-L3 | P0 = isolate HX immediately
TH-L3-007 | Thermal | Loop 3 | Host Seasonal Schedule | Host facility heating season active/inactive | DI | REST API | 0/1 | — | N | — | 3600s | HOST-API | Capacity planning input
TH-L3-008 | Thermal | Loop 3 | Host Maintenance Window | Host plant maintenance window — no export available | DI | REST API | 0/1 | — | Y | P3 | 3600s | HOST-API | Pre-schedule reject mode transition
TH-L3-009 | Thermal | Loop 3 | Host Interface Panel Status | ML-owned host interface panel — online/fault | DI | Modbus TCP | 0/1 | — | Y | P1 | 30s | HIP-01 | Communications health to host BMS
TH-L3-C01 | Thermal | Loop 3 Calc | Host Heat Utilization % | % of available export heat that host actually consumes | Calc | Derived | 0–100 | % | N | — | 300s | — | Business model effectiveness metric
TH-L3-C02 | Thermal | Loop 3 Calc | Host Savings Estimate ($/day) | Estimated host energy cost savings from ML heat | Calc | Derived | 0–9999 | $/day | N | — | 3600s | — | Host value proposition metric
TH-L3-C03 | Thermal | Loop 3 Calc | Host Availability Score | % of time host can receive heat (demand + operational) | Calc | Derived | 0–100 | % | N | — | 3600s | — | Site selection validation KPI
2.5 HEAT REJECTION SYSTEM (100% FALLBACK)
2.5.1 Dry / Adiabatic Cooler
TH-REJ-001 | Thermal | Rejection | Cooler Fan Status (×n) | Individual fan run/stop/fault per cooler unit | DI | Modbus TCP | 0/1/2 | — | Y | P1 | 5s | FAN-REJ-nn | n fans; P0 if all-fault
TH-REJ-002 | Thermal | Rejection | Cooler Fan Speed (×n) | VFD fan speed per unit — staging control feedback | AI | Modbus TCP | 0–60 | Hz | N | — | 10s | VFD-REJ-nn | Speed staging for noise/efficiency
TH-REJ-003 | Thermal | Rejection | Cooler Inlet Fluid Temp | Warm fluid inlet to dry cooler from L2 | AI | Modbus TCP | 25–65 | °C | Y | P2 | 5s | TEMP-REJ-I | Should match L2 supply temp
TH-REJ-004 | Thermal | Rejection | Cooler Outlet Fluid Temp | Cooled fluid outlet from dry cooler | AI | Modbus TCP | 10–50 | °C | Y | P1 | 5s | TEMP-REJ-O | Must be below IT setpoint requirement
TH-REJ-005 | Thermal | Rejection | Ambient Air Temperature | Outside ambient temp at cooler intake — design day reference | AI | 4-20mA | -20–50 | °C | N | — | 60s | TEMP-AMB | Performance derating reference
TH-REJ-006 | Thermal | Rejection | Ambient Relative Humidity | Outside ambient RH — adiabatic benefit calculation | AI | 4-20mA | 0–100 | %RH | N | — | 120s | RH-AMB | Adiabatic mode optimization
TH-REJ-007 | Thermal | Rejection | Cooler Fluid Flow Rate | Flow through rejection circuit | AI | Modbus TCP | 0–500 | L/min | Y | P1 | 10s | FLOW-REJ | Capacity verification
2.5.2 Adiabatic Controls (If Equipped)
TH-REJ-008 | Thermal | Rejection | Adiabatic Spray Status | Pre-cooling spray system — on/off | DI | Dry Contact | 0/1 | — | N | — | 10s | SPRAY-01 | Activated when ambient exceeds dry threshold
TH-REJ-009 | Thermal | Rejection | Adiabatic Water Consumption | Spray water flow rate / consumption | AI | Modbus TCP | 0–100 | L/h | Y | P3 | 120s | FLOW-SPRAY | Water cost and consumption tracking
TH-REJ-010 | Thermal | Rejection | Adiabatic Spray Command | Command to enable/disable adiabatic spray | DO | Dry Contact | 0/1 | — | N | — | Event | SPRAY-01 | Auto or manual control
TH-REJ-011 | Thermal | Rejection | Hygiene Cycle Active | Anti-legionella hygiene cycle status | DI | Dry Contact | 0/1 | — | Y | P3 | 300s | SPRAY-01 | Health & safety compliance
2.5.3 Rejection Fan Commands & Staging
TH-REJ-012 | Thermal | Rejection | Fan Speed Command (×n) | VFD speed setpoint per cooler fan unit | AO | Modbus TCP | 0–60 | Hz | N | — | Event | VFD-REJ-nn | Staging logic for noise/efficiency
TH-REJ-013 | Thermal | Rejection | Fan Stage Enable (×n) | Enable/disable individual cooler fan unit | DO | Modbus TCP | 0/1 | — | N | — | Event | VFD-REJ-nn | Maintenance isolation
2.5.4 Rejection Calculated Points
TH-REJ-C01 | Thermal | Rejection Calc | Rejected Thermal Power (kWt) | Heat rejected to atmosphere via dry/adiabatic cooler | Calc | Derived | 0–1200 | kWt | Y | P1 | 5s | — | → δt × flow × Cp
TH-REJ-C02 | Thermal | Rejection Calc | Rejection Capacity Available % | Current reject capacity vs design maximum | Calc | Derived | 0–100 | % | Y | P0 | 60s | — | P0 if <100% at design day ambient
TH-REJ-C03 | Thermal | Rejection Calc | Rejection Fan Power (Total) | Total electrical power consumed by rejection fans | Calc | Derived | 0–50 | kW | N | — | 60s | — | Parasitic load — affects PUE
2.6 THERMAL MODE STATE ENGINE
TH-MODE-001 | Thermal | Mode Engine | Active Operating Mode | Current thermal mode: 1=Export, 2=Mixed, 3=Reject, 4=Maint | DI | Safety PLC | 1–4 | Mode | Y | P1 | 1s | PLC-THM | Primary mode state — safety-critical
TH-MODE-002 | Thermal | Mode Engine | Mode Transition In-Progress | Mode transition currently executing | DI | Safety PLC | 0/1 | — | Y | P2 | 1s | PLC-THM | Valve repositioning in progress
TH-MODE-003 | Thermal | Mode Engine | Mode Transition Timer | Seconds elapsed in current transition | AI | Safety PLC | 0–300 | s | Y | P1 | 1s | PLC-THM | Alarm if transition exceeds timeout
TH-MODE-004 | Thermal | Mode Engine | Mode Override Active | Manual/operator mode override in effect | DI | Safety PLC | 0/1 | — | Y | P2 | 1s | PLC-THM | Alert NOC of manual control
TH-MODE-005 | Thermal | Mode Engine | Mode Command (from MCS) | Requested mode from application layer | AO | Safety PLC | 1–4 | Mode | N | — | Event | PLC-THM | Application → PLC mode request
TH-MODE-006 | Thermal | Mode Engine | Mode Confirm (from PLC) | PLC confirmation of mode achieved | DI | Safety PLC | 1–4 | Mode | Y | P1 | 1s | PLC-THM | Mismatch command vs confirm = P1
TH-MODE-007 | Thermal | Mode Engine | All Valve Positions Confirmed | All mode-dependent valves in correct position | DI | Safety PLC | 0/1 | — | Y | P0 | 1s | PLC-THM | P0 if valves mispositioned in any mode
TH-MODE-008 | Thermal | Mode Engine | Safety PLC Heartbeat | Thermal mode PLC alive/healthy indicator | DI | Safety PLC | 0/1 | — | Y | P0 | 5s | PLC-THM | P0 on loss — default to reject mode
TH-MODE-009 | Thermal | Mode Engine | Safety PLC Fault Code | Diagnostic fault code from thermal safety PLC | AI | Safety PLC | 0–999 | Code | Y | P0 | 1s | PLC-THM | Fault lookup table in MCS
TH-MODE-C01 | Thermal | Mode Calc | Time in Export Mode (Today) | Cumulative hours in export mode — current day | Calc | Derived | 0–24 | hrs | N | — | 60s | — | Revenue / host value tracking
TH-MODE-C02 | Thermal | Mode Calc | Export Mode Availability % | % of time in export mode — rolling 30 days | Calc | Derived | 0–100 | % | Y | P3 | 3600s | — | Host SLA compliance metric
TH-MODE-C03 | Thermal | Mode Calc | Mode Transitions Today | Count of mode transitions — current day | Calc | Derived | 0–999 | count | Y | P3 | Event | — | High transitions = instability alarm
2.7 THERMAL SAFETY & LEAK DETECTION
2.7.1 TPM Leak Containment
TH-SAF-001 | Thermal | Safety | Leak — TPM Drip Tray 1 (HX Area) | Drip tray under plate heat exchanger | DI | Dry Contact | 0/1 | — | Y | P0 | 1s | LEAK-TPM-01 | P0 — major leak at HX; isolate
TH-SAF-002 | Thermal | Safety | Leak — TPM Drip Tray 2 (Pump Area) | Drip tray under pump station | DI | Dry Contact | 0/1 | — | Y | P0 | 1s | LEAK-TPM-02 | P0 — pump seal or flange failure
TH-SAF-003 | Thermal | Safety | Leak — TPM Drip Tray 3 (Valve Gallery) | Drip tray under valve manifold area | DI | Dry Contact | 0/1 | — | Y | P0 | 1s | LEAK-TPM-03 | Valve packing or joint leak
TH-SAF-004 | Thermal | Safety | Leak — TPM Perimeter Rope | Rope-style leak sensor around TPM perimeter | DI | Dry Contact | 0/1 | — | Y | P1 | 1s | LEAK-TPM-ROPE | Secondary containment breach
TH-SAF-005 | Thermal | Safety | Leak — Pipe Penetration (CM-TPM) | Sensor at wall/floor penetration between Compute Module and TPM | DI | Dry Contact | 0/1 | — | Y | P0 | 1s | LEAK-PEN-01 | P0 — protect IT environment from water
TH-SAF-006 | Thermal | Safety | Sump/Drain Level — TPM | TPM containment sump water level | AI | 4-20mA | 0–100 | % | Y | P1 | 30s | LEVEL-SUMP | Rising level = undetected leak
2.7.2 Overpressure & Relief
TH-SAF-007 | Thermal | Safety | PRV Discharge — L2 Loop | Pressure relief valve has discharged on L2 | DI | Dry Contact | 0/1 | — | Y | P0 | 1s | PRV-L2 | P0 — overpressure event; investigate immediately
TH-SAF-008 | Thermal | Safety | PRV Discharge — HX Secondary | PRV discharge on host-side HX boundary | DI | Dry Contact | 0/1 | — | Y | P0 | 1s | PRV-HX-S | Cross-system pressure event
TH-SAF-009 | Thermal | Safety | Pressure Transient Alert | Rapid pressure change detected (water hammer) | DI | Safety PLC | 0/1 | — | Y | P0 | 1s | PLC-THM | PLC-derived from pressure rate of change
2.7.3 Glycol & Chemical Safety
TH-SAF-010 | Thermal | Safety | Glycol Spill — TPM Floor | Glycol spill detection sensor at low point | DI | Dry Contact | 0/1 | — | Y | P1 | 1s | SPILL-GLY-01 | Trigger ventilation increase
TH-SAF-011 | Thermal | Safety | TPM Ventilation Override Status | TPM ventilation in high-flow override mode | DI | Dry Contact | 0/1 | — | N | — | 10s | FAN-TPM-01 | Auto-activated on spill/VOC alarm
TH-SAF-012 | Thermal | Safety | Eye Wash Station Check | Eye wash station weekly test confirmation | DI | Manual/REST | 0/1 | — | Y | P3 | 86400s | MANUAL | Compliance tracking — OSHA/local regs
2.7.4 Freeze Protection (Regional)
TH-SAF-013 | Thermal | Safety | Pipe Surface Temp — Exposed Run 1 | Surface temp on exposed pipe between TPM and cooler | AI | 4-20mA | -30–50 | °C | Y | P1 | 60s | TEMP-PIPE-01 | Regional deployments — freeze risk
TH-SAF-014 | Thermal | Safety | Pipe Surface Temp — Exposed Run 2 | Surface temp on second exposed pipe section | AI | 4-20mA | -30–50 | °C | Y | P1 | 60s | TEMP-PIPE-02 | Redundant sensing
TH-SAF-015 | Thermal | Safety | Trace Heating Status | Electric trace heating circuit — energized/off/fault | DI | Dry Contact | 0/1/2 | — | Y | P1 | 60s | TRACE-01 | Must be energized below 5°C ambient
TH-SAF-016 | Thermal | Safety | Trace Heating Command | Enable/disable trace heating | DO | Dry Contact | 0/1 | — | N | — | Event | TRACE-01 | Auto-enable on low ambient temp
TH-SAF-C01 | Thermal | Safety Calc | Freeze Risk Score | Composite score from pipe temps, ambient, glycol concentration | Calc | Derived | 0–100 | score | Y | P1 | 300s | — | High score = increase monitoring frequency
TH-SAF-C02 | Thermal | Safety Calc | Thermal Safety Summary | Composite all-clear / attention / alarm state for TPM | Calc | Derived | 0–2 | State | Y | P0 | 5s | — | 0=All-clear, 1=Attention, 2=Alarm

## Protocols & Hardware
COMMUNICATION PROTOCOLS & HARDWARE REGISTER
Protocol | Layer | Typical Devices | Port / Bus | Notes
Modbus TCP | Field → Edge | Power meters, PDUs, pumps, VFDs, flow meters, CDUs | TCP/502 | Most common industrial protocol in MicroLink deployments; 1-second polling typical
Modbus RTU | Field → Edge | Legacy sensors, local instruments on RS-485 bus | RS-485 | Used where TCP not available; gateway converts to TCP at edge
BACnet/IP | Field → Edge | HVAC units, host BMS interface, room controllers | UDP/47808 | Primary protocol for host facility integration and environmental monitoring
SNMP v2c/v3 | Field → Edge | UPS, network switches, IP cameras, NVR, PDUs | UDP/161 | v3 preferred for authentication; v2c where vendor mandates
MQTT | Edge → Cloud | Edge gateway telemetry, IoT sensors, heartbeat | TCP/8883 | TLS-encrypted; QoS 1 for telemetry; QoS 2 for commands
OPC UA | Field → Edge | Industrial PLCs, advanced CDUs, thermal PLC | TCP/4840 | Secure; used for complex data structures from PLC/SCADA tier
4-20mA | Sensor → I/O | Pressure transducers, level sensors, some flow meters | Analog | Hardwired to edge I/O module; most reliable for safety-critical
Dry Contact | Sensor → I/O | Door switches, leak sensors, relay outputs, fire panel | Digital I/O | Voltage-free contacts; most robust for binary signals
ONVIF | Camera → NVR | IP security cameras — streaming & event notification | TCP/HTTP | Standard for cross-vendor camera integration
OSDP | Reader → Panel | Badge readers, electronic locks | RS-485 | Modern secure access control protocol replacing Wiegand
REST API | App → App | Host portal, colo partner API, billing system, MCS internal | HTTPS/443 | JSON payloads; OAuth2 auth; rate-limited external access
gNMI/gRPC | Network → Edge | Streaming network telemetry from routers/switches | TCP/9339 | High-frequency telemetry for network performance monitoring
Safety PLC | PLC → Edge | Thermal mode controller, safety interlocks | Profinet/OPC | Dedicated safety-rated PLC for thermal mode state machine
ICMP | Network Probe | Latency and availability probes to IX/MMR | IP | Synthetic monitoring for SLA compliance